## Neutral Current - Split WYE-I
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY |  |  |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
Split-Wye Neutral Current Relay Settings Sheet for Use Current Sensing Relay
Project Information
Customer Name: | Enter Name |  | Project Name: | Enter Project Name
Stage Number(s) | Enter Stage #
Stage kvar | Enter stage kvar
Background Information
Neutral Current Relay Settings
Relays Should Be Set to Trip Before Remaining Capacitor Voltage Exceeds Capacitor Maxium Volage Rating
[7 empty] | N-G | Remaining | Neutral | CT | Recommended | Recommended
[7 empty] | Voltage | Cap Voltage | Current | Secondary Current | Relay Setting | Relay Setting | Factory
[6 empty] | Caps out | (Volts) | (Volts) | (amps) | (amps) | Primary Amps * | Secondary amps | Setting
[6 empty] | 1 | 1441.6185 | 8649.711 | 7.5852 | 0.37926 | 4.5511 | 0.22756 | ALARM
[6 empty] | 2 | 3604.0462 | 10812.1387 | 16.6874 | 0.83437 | 10.0125 | 0.50062 | TRIP
[6 empty] | 3 | 7208.0925 | 14416.185 | 27.8124 | 1.3906 | 16.6874 | 0.83437 | N/A
[6 empty] | 4 | 14416.185 | 21624.2775 | 41.7186 | 2.0859 | 25.0312 | 1.2516 | N/A
[6 empty] | 5 | 36040.4624 | 43248.5549 | 59.598 | 2.9799 | 35.7588 | 1.7879 | N/A
[7 empty] | Nominal Cap Voltage | 7200 | Volts | * Harmonic Filter Banks should be set to trip and alarm on first capacitor fuse operation.
[7 empty] | Maximum Voltage | 7920 | Volts
Capacitor Bank/Stage Data
Enter Capacitor Bank Line-to-Line Voltage (kV) |  | 12.47 | This value is the line to line voltage in kV that the capacitor bank or harmonic filter bank is applied at.
Enter effective kvar output of filter/capacitor bank stage (kvar) |  | 600 | This is the 3-phase output kvar of the stage (enter as kvar not Mvar) at nominal system voltage.
Normal Phase Current (INOMINAL) |  | 27.8124 | (amps)
Number of Capacitors per Stage (N) per Phase |  | 2 | (This includes caps on both sides of wye - on a per phase basis - i.e. caps in parallel). Assumes all capacitors are equal in size.
Neutral CT Ratio |  | 20 | (primary divided by secondary)
Enter Capacitor Voltage Rating (kV) |  | 7.2 | This is the nameplate voltage rating of capacitor in kV
Northeast Power Systems, Inc.
Split-Wye Neutral Current Relay Settings - Enter Name, Enter Project Name Project - Page 2 Settings for Stage -Enter Stage #
Results for 1 Failed Capacitor
Number of failed capacitors per phase (F) |  | 1 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 8649.711 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 1441.6185 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 7.5852 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 20.13% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 0.37926 | (amps)
Suggested Relay Setting (primary amps) |  | 4.5511 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 0.22756 | (amps) Based on 60% of expected CT secondary current
Results for 2 Failed Capacitors
Number of failed capacitors per phase (F) |  | 2 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 10812.1387 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 3604.0462 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 16.6874 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 50.17% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 0.83437 | (amps)
Suggested Relay Setting (primary amps) |  | 10.0125 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 0.50062 | (amps) Based on 60% of expected CT secondary current
Results for 3 Failed Capacitors
Number of failed capacitors per phase (F) |  | 3 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 14416.185 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 7208.0925 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 27.8124 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 100.2% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 1.3906 | (amps)
Suggested Relay Setting (primary amps) |  | 16.6874 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 0.83437 | (amps) Based on 60% of expected CT secondary current
Results for 4 Failed Capacitors
Number of failed capacitors per phase (F) |  | 4 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 21624.2775 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 14416.185 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 41.7186 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 200.3% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 2.0859 | (amps)
Suggested Relay Setting (primary amps) |  | 25.0312 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 1.2516 | (amps) Based on 60% of expected CT secondary current
Results for 5 Failed Capacitors
Number of failed capacitors per phase (F) |  | 5 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 43248.5549 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 36040.4624 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 59.598 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 500.7% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 2.9799 | (amps)
Suggested Relay Setting (primary amps) |  | 35.7588 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 1.7879 | (amps) Based on 60% of expected CT secondary current
  To prevent capacitor damage on the remaining capacitors on a capacitor bank with one or more fuse operatons. This is true for ungrounded banks due to a capacitor neutral shift that occurs from a missmatch in capactive reactance between each phase. The neutral shift is more prevalent with stages or banks that have less than 4 capacitors per phase. Grounded banks and Delta connected banks are not subjected to this concern. In no event should the blown fuse detection system allow the capacitor voltage to exceed its rating by 10%. Capacitor voltage can be determined from the equations below.
  To alert plant personnel of a blown fuse condition.
  To prevent unbalance var support that can lead to system voltage unbalance. Typically, power systems should not be operated with more than 2% voltage unbalance.
  To prevent harmonic filter bank de-tuning. Generally, NEPSI's filter banks are designed to trip on the operation of a single fuse to elleviate or lesson this concern.
This spreadsheet provides calculation assistance for determing blown fuse trip and alarm setpoints for overcurrent relays used in conjunction with split-wye connected capacitor banks and harmonic filter banks. The relay works with a signal derived from a current transformer (CT) mounted in the neutral between two wye-connected capacitor banks as shown in the figure to the right. Relay calibration should be done using primary current injection at the neutral CT or secondary current injection at the CT.
Capacitor Banks are normally equipped with blown fuse detection for the following reasons:
Equations from IEEE C37.99-1980 – IEEE Guide for Protection of Shunt Capacitor Banks provide a simple means for the calculation of expected capacitor voltage, neutral-to-ground voltage shift, and current flow between wye connected capacitor banks for for one or more failed capacitors. Formulas are as follows:
Where
  ICURRENT THROUGH NEUTRAL CT = Current in amps through CT for one or more capacitor fuse operations
  INOMINAL = Phase Current of Entire Capacitor Bank (Both Wye-Connected Banks Combined in amps)
  VØ = Nominal Phase-to-Neutral System Voltage (volts)
  F = Number of Failed Capacitors per Phase
  N = Number of Capacitors per Phase (this includes both sides of wye for split wye banks)
  VREMAINING CAPACITOR VOLTAGE = Voltage remaining on capacitor after fuse operation (volts)
  VCAP BANK NEUTRAL-TO-GROUND = Voltage from Capacitor BAnk neutral to ground after fuse(s) operation.
The relay should be set to trip at 60% of CT secondary current for the condition that results in more than 10% over-voltage on the remaining capacitors. A time delay of 10 seconds is recommended. For relays with two setpoints, NEPSI recommends that one setpoint be used to alarm on the first fuse operation. The second set-point should be used to trip the bank off line that results in excessive over-voltage (10% over-voltage based on capacitor voltage rating). Filter banks should be set to trip and alarm for the first fuse operation (one failed capacitor) as filter detuning can occur.
Contact NEPSI at 518-792-4776 or paul.steciuk@nepsi.com for additional assistance in setting neutral current/voltage relays for the purpose of blown fuse protection on capacitor banks.
(VOLTS)
𝑉_(𝑅𝐸𝑀𝐴𝐼𝑁𝐼𝑁𝐺 𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅 𝑉𝑂𝐿𝑇𝐴𝐺𝐸 )=(𝑉_(Ø ×) 𝑁×3)/(3𝑁−𝐹) (VOLTS)
(VOLTS)
𝑉_( 𝐶𝐴𝑃 𝐵𝐴𝑁𝐾 𝑁𝐸𝑈𝑇𝑅𝐴𝐿−𝑇𝑂−𝐺𝑅𝑂𝑈𝑁𝐷 )=(𝑉_(Ø ×) 𝐹)/(3𝑁−𝐹) (VOLTS)
(AMPS)
𝐼_(𝐶𝑈𝑅𝑅𝐸𝑁𝑇 𝑇𝐻𝑅𝑂𝑈𝐺𝐻 𝑁𝐸𝑈𝑇𝑅𝐴𝐿 𝐶𝑇)=(𝐼_(𝑁𝑂𝑀𝐼𝑁𝐴𝐿 ×) 3×𝐹)/(6𝑁−𝐹) (AMPS)
(AMPS)
𝐼_𝑁𝑂𝑀𝐼𝑁𝐴𝐿=𝐼_(𝐶𝐴𝑃 𝐵𝐴𝑁𝐾 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=(𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅 𝐵𝐴𝑁𝐾 3∅ 𝐾𝑉𝐴𝑅 𝑅𝐴𝑇𝐼𝑁𝐺)/(1.73×〖𝐾𝑉〗_𝐿𝐿 ) (AMPS)

## Neutral Current - Split WYE-V
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY | [6 empty] | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
Split-Wye Neutral Current Relay Settings Sheet for Use with Voltage Sensing Relay
Project Information
Customer Name: | Enter Customer Name |  | Project Name: | Enter Project Name
Stage Number(s) | Enter Stage Number
Stage kvar | Enter stage kvar
Background Information
Neutral Current Relay Settings
Relays Should Be Set to Trip Before Remaining Capacitor Voltage Exceeds Capacitor Maxium Volage Rating
[9 empty] | N-G | Remaining | Neutral | CT | Recommended | Recommended
[9 empty] | Voltage | Cap Voltage | Current | Secondary Current | Relay Setting | Relay Setting | Factory
[8 empty] | Caps out | (Volts) | (Volts) | (amps) | (amps) | Primary Amps * | Secondary amps | Setting
[8 empty] | 1 | 1173.0704 | 21115.2669 | 17.2333 | 0.86167 | 10.34 | 0.517 | ALARM
[8 empty] | 2 | 2492.7746 | 22434.9711 | 35.4804 | 1.774 | 21.2882 | 1.0644 | TRIP
[8 empty] | 3 | 3988.4393 | 23930.6358 | 54.8333 | 2.7417 | 32.9 | 1.645 | N/A
[8 empty] | 4 | 5697.7704 | 25639.967 | 75.3958 | 3.7698 | 45.2375 | 2.2619 | N/A
[8 empty] | 5 | 7670.0756 | 27612.2721 | 97.2849 | 4.8642 | 58.371 | 2.9185 | N/A
[9 empty] | Nominal Cap Voltage | 19920 | Volts | * Harmonic Filter Banks should be set to trip and alarm on first capacitor fuse operation.
[9 empty] | Maximum Voltage | 21912 | Volts
Capacitor Bank/Stage Data
Enter Capacitor Bank Line-to-Line Voltage (kV) |  | 34.5 | This value is the line to line voltage in kV that the capacitor bank or harmonic filter bank is applied at.
Enter effective kvar output of filter/capacitor bank stage (kvar) |  | 12000 | This is the 3-phase output kvar of the stage (enter as kvar not Mvar) at nominal system voltage.
Normal Phase Current (INOMINAL) |  | 201.0555 | (amps)
Number of Capacitors per Stage (N) per Phase |  | 6 | (This includes caps on both sides of wye - on a per phase basis - i.e. caps in parallel). Assumes all capacitors are equal in size.
Neutral CT Ratio |  | 20 | (primary divided by secondary)
Enter resistance of burden resistor (ohms) |  | 10 | (ohms)
Enter Capacitor Voltage Rating (kV) |  | 19.92 | This is the nameplate voltage rating of capacitor in kV
Northeast Power Systems, Inc.
Split-Wye Neutral Current Relay Settings - Enter Customer Name, Enter Project Name Project - Page 2 Settings for Stage -Enter Stage Number
Results for 1 Failed Capacitor
Number of failed capacitors per phase (F) |  | 1 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 21115.2669 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 1173.0704 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 17.2333 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 6% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 0.86167 | (amps) | Burden Volts | 8.6167 | (volts)
|  |  |  | Burden Watts | 7.4247 | (watts)
Suggested Relay Setting (primary amps) |  | 10.34 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 0.517 | (amps) Based on 60% of expected CT secondary current
Results for 2 Failed Capacitors
Number of failed capacitors per phase (F) |  | 2 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 22434.9711 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 2492.7746 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 35.4804 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 12.63% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 1.774 | (amps) | Burden Volts | 17.7402 | (volts)
|  |  |  | Burden Watts | 31.4715 | (watts)
Suggested Relay Setting (primary amps) |  | 21.2882 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 1.0644 | (amps) Based on 60% of expected CT secondary current
Results for 3 Failed Capacitors
Number of failed capacitors per phase (F) |  | 3 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 23930.6358 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 3988.4393 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 54.8333 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 20.13% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 2.7417 | (amps) | Burden Volts | 27.4167 | (volts)
|  |  |  | Burden Watts | 75.1674 | (watts)
Suggested Relay Setting (primary amps) |  | 32.9 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 1.645 | (amps) Based on 60% of expected CT secondary current
Results for 4 Failed Capacitors
Number of failed capacitors per phase (F) |  | 4 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 25639.967 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 5697.7704 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 75.3958 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 28.71% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 3.7698 | (amps) | Burden Volts | 37.6979 | (volts)
|  |  |  | Burden Watts | 142.1133 | (watts)
Suggested Relay Setting (primary amps) |  | 45.2375 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 2.2619 | (amps) Based on 60% of expected CT secondary current
Results for 5 Failed Capacitors
Number of failed capacitors per phase (F) |  | 5 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 27612.2721 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 7670.0756 | (Volts)
Neutral Current Between Wye Banks (ICURRENT THROUGH NEUTRAL CT) |  | 97.2849 | (Amps) This is the primary current through the neutral current transformer.
Percent Over-voltage on Failed Capacitor |  | 38.62% | (Should not be greater than 10% under nominal system conditions)
CT Secondary amps (amps to relay) |  | 4.8642 | (amps) | Burden Volts | 48.6425 | (volts)
|  |  |  | Burden Watts | 236.609 | (watts)
Suggested Relay Setting (primary amps) |  | 58.371 | (amps) Based on 60% of the ICURENT THROUGH NEUTRAL CT
Suggested Relay Setting (Secondary amps) |  | 2.9185 | (amps) Based on 60% of expected CT secondary current
  To prevent capacitor damage on the remaining capacitors on a capacitor bank with one or more fuse operatons. This is true for ungrounded banks due to a capacitor neutral shift that occurs from a missmatch in capactive reactance between each phase. The neutral shift is more prevalent with stages or banks that have less than 4 capacitors per phase. Grounded banks and Delta connected banks are not subjected to this concern. In no event should the blown fuse detection system allow the capacitor voltage to exceed its rating by 10%. Capacitor voltage can be determined from the equations below.
  To alert plant personnel of a blown fuse condition.
  To prevent unbalance var support that can lead to system voltage unbalance. Typically, power systems should not be operated with more than 2% voltage unbalance.
  To prevent harmonic filter bank de-tuning. Generally, NEPSI's filter banks are designed to trip on the operation of a single fuse to elleviate or lesson this concern.
This spreadsheet provides calculation assistance for determing blown fuse trip and alarm setpoints for relays used in conjunction with split-wye connected capacitor banks and harmonic filter banks. The relay works with a signal derived from a current transformer (CT) mounted in the neutral between two wye-connected capacitor banks as shown in the figure to the right. The relay may be an over-current relay with trip settings based on current or may be an over-voltage relay with trip settings based on voltage. When a voltage relay is used (such as the Basler Basler BE1-59NC, a burden resistor is connected accross the CT secondary to convert the CT secondary current signal to a voltage signal. Relay calibration should be done using primary current injection at the neutral CT or secondary current injection at the CT.
Capacitor Banks are normally equipped with blown fuse detection for the following reasons:
Equations from IEEE C37.99-1980 – IEEE Guide for Protection of Shunt Capacitor Banks provide a simple means for the calculation of expected capacitor voltage, neutral-to-ground voltage shift, and current flow between wye connected capacitor banks for for one or more failed capacitors. Formulas are as follows:
Where
  ICURRENT THROUGH NEUTRAL CT = Current in amps through CT for one or more capacitor fuse operations
  INOMINAL = Phase Current of Entire Capacitor Bank (Both Wye-Connected Banks Combined in amps)
  VØ = Nominal Phase-to-Neutral System Voltage (volts)
  F = Number of Failed Capacitors per Phase
  N = Number of Capacitors per Phase (this includes both sides of wye for split wye banks)
  VREMAINING CAPACITOR VOLTAGE = Voltage remaining on capacitor after fuse operation (volts)
  VCAP BANK NEUTRAL-TO-GROUND = Voltage from Capacitor BAnk neutral to ground after fuse(s) operation.
The relay should be set to trip at 60% of CT secondary current or burden voltage for the condition that results in more than 10% over-voltage on the remaining capacitors. A time delay of 10 seconds is recommended. For relays with two setpoints, NEPSI recommends that one setpoint be used to alarm on the first fuse operation. The second set-point should be used to trip the bank off line that results in excessive over-voltage (10% over-voltage based on capacitor voltage rating). Filter banks should be set to trip and alarm for the first fuse operation (one failed capacitor) as filter detuning can occure.
Contact NEPSI at 518-792-4776 or paul.steciuk@nepsi.com for additional assistance in setting neutral current/voltage relays for the purpose of blown fuse protection on capacitor banks.
(VOLTS)
𝑉_(𝑅𝐸𝑀𝐴𝐼𝑁𝐼𝑁𝐺 𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅 𝑉𝑂𝐿𝑇𝐴𝐺𝐸 )=(𝑉_(Ø ×) 𝑁×3)/(3𝑁−𝐹) (VOLTS)
(VOLTS)
𝑉_( 𝐶𝐴𝑃 𝐵𝐴𝑁𝐾 𝑁𝐸𝑈𝑇𝑅𝐴𝐿−𝑇𝑂−𝐺𝑅𝑂𝑈𝑁𝐷 )=(𝑉_(Ø ×) 𝐹)/(3𝑁−𝐹) (VOLTS)
(AMPS)
𝐼_(𝐶𝑈𝑅𝑅𝐸𝑁𝑇 𝑇𝐻𝑅𝑂𝑈𝐺𝐻 𝑁𝐸𝑈𝑇𝑅𝐴𝐿 𝐶𝑇)=(𝐼_(𝑁𝑂𝑀𝐼𝑁𝐴𝐿 ×) 3×𝐹)/(6𝑁−𝐹) (AMPS)
(AMPS)
𝐼_𝑁𝑂𝑀𝐼𝑁𝐴𝐿=𝐼_(𝐶𝐴𝑃 𝐵𝐴𝑁𝐾 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=(𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅 𝐵𝐴𝑁𝐾 3∅ 𝐾𝑉𝐴𝑅 𝑅𝐴𝑇𝐼𝑁𝐺)/(1.73×〖𝐾𝑉〗_𝐿𝐿 ) (AMPS)

## Neutral Voltage
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY |  |  |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
Neutral Voltage Unbalance Protection Relay Settings Sheet
Project Information
Customer Name: | Enter Customer Name |  | Project Name: | Enter Project Name
Stage Number(s) | Enter Stage Number
Stage kvar | Enter Stage kvar
Background Information
Neutral Voltage Relay Settings
Relays Should Be Set to Trip Before Remaining Capacitor Voltage Exceeds Capacitor Maxium Volage Rating
[7 empty] | N-G | Remaining | Neutral PT | Neutral PT | Recommended | Recommended
[7 empty] | Voltage | Cap Voltage | Primary Volts | Seconary Volts | Relay Setting | Relay Setting | Factory
[6 empty] | Caps out | (Volts) | (Volts) | (Volts) | (Volts) | Primary Volts * | Secondary Volts | Setting
[6 empty] | 1 | 1173.0704 | 21115.2669 | 1173.0704 | 4.0802 | 703.8422 | 2.4481 | ALARM
[6 empty] | 2 | 2492.7746 | 22434.9711 | 2492.7746 | 8.6705 | 1495.6647 | 5.2023 | TRIP
[6 empty] | 3 | 3988.4393 | 23930.6358 | 3988.4393 | 13.8728 | 2393.0636 | 8.3237 | N/A
[6 empty] | 4 | 5697.7704 | 25639.967 | 5697.7704 | 19.8183 | 3418.6623 | 11.891 | N/A
[6 empty] | 5 | 7670.0756 | 27612.2721 | 7670.0756 | 26.6785 | 4602.0454 | 16.0071 | N/A
[7 empty] | Nominal Cap Voltage | 19920 | Volts | * Harmonic Filter Banks should be set to trip and alarm on first capacitor fuse operation.
[7 empty] | Maximum Voltage | 21912 | Volts
Capacitor Bank/Stage Data
Enter Capacitor Bank Line-to-Line Voltage (kV) |  | 34.5 | This value is the line to line voltage in kV that the capacitor bank or harmonic filter bank is applied at.
Enter effective kvar output of filter/capacitor bank stage (kvar) |  | 12000 | This is the 3-phase output kvar of the stage (enter as kvar not Mvar) at nominal system voltage.
Normal Phase Current (INOMINAL) |  | 201.0555 | (amps)
Number of Capacitors per Stage per Phase (N) |  | 6 | Assumes all capacitors are of equal size.
Neutral PT Ratio |  | 287.5 | (primary divided by secondary)
Enter Capacitor Voltage Rating (kV) |  | 19.92 | This is the nameplate voltage rating of capacitor in kV
Northeast Power Systems, Inc.
Split-Wye Neutral Current Relay Settings - Enter Customer Name, Enter Project Name Project - Page 2 Settings for Stage -Enter Stage Number
Results for 1 Failed Capacitor
Number of failed capacitors per phase (F) |  | 1 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 21115.2669 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 1173.0704 | (Volts)
Neutral PT Secondary Voltage |  | 4.0802
Percent Over-voltage on Failed Capacitor |  | 6% | (Should not be greater than 10% under nominal system conditions)
Suggested Relay Setting (Primary volts) |  | 703.8422 | (Volts) Based on 60% of the VNEUTRAL TO GROUND Voltage
Suggested Relay Setting (Secondary volts) |  | 2.4481 | (Volts) Based on 60% of expected PT Voltage
Results for 2 Failed Capacitor
Number of failed capacitors per phase (F) |  | 2 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 22434.9711 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 2492.7746 | (Volts)
Neutral PT Secondary Voltage |  | 8.6705
Percent Over-voltage on Failed Capacitor |  | 12.63% | (Should not be greater than 10% under nominal system conditions)
Suggested Relay Setting (Primary volts) |  | 1495.6647 | (Volts) Based on 60% of the VNEUTRAL TO GROUND Voltage
Suggested Relay Setting (Secondary volts) |  | 5.2023 | (Volts) Based on 60% of expected PT Voltage
Results for 3 Failed Capacitor
Number of failed capacitors per phase (F) |  | 3 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 23930.6358 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 3988.4393 | (Volts)
Neutral PT Secondary Voltage |  | 13.8728
Percent Over-voltage on Failed Capacitor |  | 20.13% | (Should not be greater than 10% under nominal system conditions)
Suggested Relay Setting (Primary volts) |  | 2393.0636 | (Volts) Based on 60% of the VNEUTRAL TO GROUND Voltage
Suggested Relay Setting (Secondary volts) |  | 8.3237 | (Volts) Based on 60% of expected PT Voltage
Results for 4 Failed Capacitor
Number of failed capacitors per phase (F) |  | 4 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 25639.967 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 5697.7704 | (Volts)
Neutral PT Secondary Voltage |  | 19.8183
Percent Over-voltage on Failed Capacitor |  | 28.71% | (Should not be greater than 10% under nominal system conditions)
Suggested Relay Setting (Primary volts) |  | 3418.6623 | (Volts) Based on 60% of the VNEUTRAL TO GROUND Voltage
Suggested Relay Setting (Secondary volts) |  | 11.891 | (Volts) Based on 60% of expected PT Voltage
Results for 5 Failed Capacitor
Number of failed capacitors per phase (F) |  | 5 | (Normally 1 or more cans are allowed to fail for banks consisting of 4 or more total per phase)
Voltage on remaining capacitors (VREMAINING CAPACITOR VOLTAGE) |  | 27612.2721 | (Volts) This is the voltage across the healthy capacitors. It should not exceed 110% of the voltage rating of the capacitor.
Neutral-to-Ground Voltage (VNEUTRAL TO GROUND) |  | 7670.0756 | (Volts)
Neutral PT Secondary Voltage |  | 26.6785
Percent Over-voltage on Failed Capacitor |  | 38.62% | (Should not be greater than 10% under nominal system conditions)
Suggested Relay Setting (Primary volts) |  | 4602.0454 | (Volts) Based on 60% of the VNEUTRAL TO GROUND Voltage
Suggested Relay Setting (Secondary volts) |  | 16.0071 | (Volts) Based on 60% of expected PT Voltage
  To prevent capacitor damage on the remaining capacitors on a capacitor bank with one or more fuse operatons. This is true for ungrounded banks due to a capacitor neutral shift that occurs from a missmatch in capactive reactance between each phase. The neutral shift is more prevalent with stages or banks that have less than 4 capacitors per phase. Grounded banks and Delta connected banks are not subjected to this concern. In no event should the blown fuse detection system allow the capacitor voltage to exceed its rating by 10%. Capacitor voltage can be determined from the equations below.
  To alert plant personnel of a blown fuse condition.
  To prevent unbalance var support that can lead to system voltage unbalance. Typically, power systems should not be operated with more than 2% voltage unbalance.
  To prevent harmonic filter bank de-tuning. Generally, NEPSI's filter banks are designed to trip on the operation of a single fuse to elleviate or lesson this concern.
This spreadsheet provides calculation assistance for determing blown fuse trip and alarm setpoints for relays used in conjunction with ungrounded wye-connected capacitor banks and harmonic filter banks. The relay works with a signal derived from a potential transformer (PT) mounted in the neutral of the capacitor bank as shown in the figure to the right. The relay is typically a over-voltage relay with trip settings based on voltage. Relay calibration is typically done by connecting voltage test set leads to the secondary leads of the PT or by connecting directly to the voltage inputs of the relay.
    CAUTION - THE PT SECONDARY LEADS SHOULD BE DISCONNECTED FROM THE PT DURING RELAY CALIBRATION AS LETHAL VOLTAGES CAN BE TRANSFORMERED ONTO THE NEUTRAL OF THE CAPACITOR BANK DURING TESTING.
Capacitor Banks are normally equipped with blown fuse detection for the following reasons:
Equations from IEEE C37.99-1980 – IEEE Guide for Protection of Shunt Capacitor Banks provide a simple means for the calculation of expected capacitor voltage, neutral-to-ground voltage shift, and current flow between wye connected capacitor banks for for one or more failed capacitors. Formulas are as follows:
Where
  F = Number of Failed Capacitors per Phase
  N = Number of Capacitors per Phase (included on both sides of wye connected capacitor bank)
  VØ = Nominal Phase-to-Neutral System Voltage (volts)
  VREMAINING CAPACITOR VOLTAGE = Voltage remaining on capacitor after fuse operation (volts)
  VCAP BANK NEUTRAL-TO-GROUND = Voltage from Capacitor BAnk neutral to ground after fuse(s) operation.
The relay should be set to trip at 60% of PT voltage for the condition that results in more than 10% over-voltage on the remaining capacitors. A time delay of 10 seconds is recommended. For relays with two setpoints, NEPSI recommends that one setpoint be used to alarm on the first fuse operation. The second set-point should be used to trip the bank off line that results in excessive over-voltage (10% over-voltage based on capacitor voltage rating). Filter banks should be set to trip and alarm for the first fuse operation (one failed capacitor) as filter detuning can occur.
Contact NEPSI at 518-792-4776 or paul.steciuk@nepsi.com for additional assistance in setting neutral current/voltage relays for the purpose of blown fuse protection on capacitor banks.
    Note: Ground faults on the source feeding medium voltage capcitor banks using neutral voltage sensing for blown fuse detection are subject to nuisance tripping as the source side ground fault results in a neutral-to-ground voltage that is seen by the neutral voltage relay. The relay time delay may be increased to ride through these types of events.
(VOLTS)
𝑉_(𝑅𝐸𝑀𝐴𝐼𝑁𝐼𝑁𝐺 𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅 𝑉𝑂𝐿𝑇𝐴𝐺𝐸 )=(𝑉_(Ø ×) 𝑁×3)/(3𝑁−𝐹) (VOLTS)
(VOLTS)
𝑉_( 𝐶𝐴𝑃 𝐵𝐴𝑁𝐾 𝑁𝐸𝑈𝑇𝑅𝐴𝐿−𝑇𝑂−𝐺𝑅𝑂𝑈𝑁𝐷 )=(𝑉_(Ø ×) 𝐹)/(3𝑁−𝐹) (VOLTS)

## Burden Calculation
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY |  |  |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
Split-Wye Neutral Current CT Burden Calculation
Project Information
Customer Name: | Enter Customer Name |  | Project Name: | Enter Project Name
Stage Number(s) | Enter Stage Number |  | CT Part #: | Enter Current Transformer Part Number
Stage kvar | Inter Stage kvar |  | CT Ratio: | Enter Current Transformer Turns Ratio
|  |  | CT Manufacturer: | Enter Current Transformer manufacturer
|  |  | CT Relay Accuracy: | Enter Current Transformer Relay Accuracy
|  |  | CT Meter Accuracy: | 0.6B0.1, 1.2B0.2, 2.4B0.5 (for example)
Background Information
Capacitor Bank - Neutral Current CT Burden Calculation
Enter CT Secondary Winding Resistance (Ohms) |  | 0.027 | (ohms) - provided by CT manufacturer
Enter CT Secondary Conductor |  | AWG10/Copper | Provided by Customer
Enter CT Secondary Conductor Impedance (ohms/1000 feet) |  | 1.1 | (ohms/1000') - Data from National Bureau of Standards Handbook 100, ROP 6-218
Enter Secondary Distance Between Relay and CT |  | 330 | (feet) This should include up, down, and over distance (total length in feet).
Calculated CT Secondary Lead Resistance |  | 0.726 | (ohms) - Value equals the product of 2 times the secondary distance and conductor impedance divided by 1000
Enter Neutral Burden Resistor Rating (ohms) |  | 10 | (ohms) - Use 0 ohms if using a current sensing relay.
Enter Burden Resistance of Neutral Relay |  | 200 | (ohms) - if in VA, convert to impedance in ohms at rated sensing voltage
Parallel combination of Neutral Burden Resistor and Neutral Relay Burden Resistance |  | 9.5238 | (ohms)
Total CT Burden Resistance |  | 10.2768 | (ohms) - Includes the series combination of CT secondary resistance, Secondary Lead Length, and the Parallel Combination of Neutral Burden Reistor and Neutral Relay Burden Resistance.
Enter Relay CT Secondary Trip Current from relay settings sheet |  | 1.06 | (amps) - The value at which the relay is expected to trip the bank offline
CT Secondary Voltage |  | 10.8934 | (volts) - product of total CT burden Resistance and relay trip current in amps
This spreadsheet provides calculation assistance for determining the CT burden voltage on neutral current transformers applied in the neutral of capacitor banks for blown fuse detection. This spreadsheet calculation assumes the use of a neutral voltage relay and neutral burden resistor connected accross the CT secondary. The neutral resistor developes a neutral voltage from the CT secondary current to provide the necessary voltage signal to the Neutral Voltage Relay. CT secondary lead length (distance between the CT and the relay), CT secondary lead impedance, neutral relay burden resistance, and CT secondary winding resistance are required for the calculation.
The secondary burden resistance is calculated by adding the series combination of the CT winding resistance to the CT Secondary Lead Resistance, to the parallel combination of the relay burden resistance and neutral CT burden resistor.
The burden voltage voltage is calculated at the CT secondary trip current rating and is calculated by multipling the total secondary burden resistance by the secondary relay trip current.
The burden voltage should be near or less than the CT relay accuracy rating or "C" rating or within the CT Meter Accuracy Rationg of the CT. For example, a meter accuracy rating of 2.4B0.5 would mean that a CT connected to a total burden impedance of 0.5 ohms would have 2.4% accuracy at full rated primary amps. If the burden ohms exceeds the meter burden ratings of the CT, the use of the "C" rating is necessary or the use of excitation curves at the trip current rating are necessary to calculate the ratio error of the CT.
For positive pickup, NEPSI sets its relay at 60% of the expected blown fuse value. Therefore, accuracies within 10% are considered sufficient for positive relay pickup for a blown fuse condition.