## _SSC (hidden)
_Ctrl_1 | {"WidgetClassification":0,"State":1,"SliderFlavor":1,"MinValue":0,"MaxValue":100,"TickInterval":0,"ShowTextbox":false,"ShowValueInTooltip":true,"IsRangeSlider":false,"CellName":"_Ctrl_1","CellAddress":"='Sheet1'!$J$7","WidgetName":6,"HiddenRow":1,"SheetCodeName":null,"ControlId":null} | {"IsHide":false,"SheetId":0,"Name":"RVSS +actiVAR Calculations","HiddenRow":0,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}} | {"ButtonStyle":0,"Name":"","HideSscPoweredlogo":false,"CopyProtect":{"IsEnabled":false,"DomainName":""},"Theme":{"BgColor":"#FFFFFFFF","BgImage":"","InputBorderStyle":2},"Layout":0,"SmartphoneSettings":{"ViewportLock":true,"UseOldViewEngine":false,"EnableZoom":false,"EnableSwipe":false,"HideToolbar":false,"InheritBackgroundColor":false,"CheckboxFlavor":1},"SmartphoneTheme":0,"InputDetection":1,"Toolbar":{"Position":1,"IsSubmit":false,"IsPrint":true,"IsPrintAll":false,"IsReset":true,"IsUpdate":false},"AspnetConfig":{"BrowseUrl":"http://localhost/ssc","FileExtension":0},"ConfigureSubmit":{"IsShowCaptcha":false,"IsUseSscWebServer":true,"ReceiverCode":"peter.steciuk@nepsi.com","IsFreeService":false,"IsAdvanceService":true,"IsDemonstrationService":false,"AfterSuccessfulSubmit":"","AfterFailSubmit":"","AfterCancelWizard":"","IsUseOwnWebServer":false,"OwnWebServerURL":"","OwnWebServerTarget":"","SubmitTarget":0},"Flavor":0,"Edition":3,"IgnoreBgInputCell":false} | {"Captcha":{"Heading":"Enter the number displayed below.","Message":"This is to verify that you are a human visitor, to prevent automated form submissions.","OkButton":"OK","CancelButton":"Cancel","ErrorMessage":"Your answer is incorrect, please try again."},"RequiredField":{"ErrorMessage":"The fields with the red border are required.","OkButton":"OK","DDLDefaultRequiredText":"Please Select"},"WizardButton":{"Next":"Next","Previous":"Previous","Cancel":"Cancel","Finish":"Finish"},"ToolbarButton":{"Submit":"Submit","Print":"Print","PrintAll":"Print All","Reset":"Reset","Update":"Update","Back":"Back"},"BrowserAndLocation":{"Browsers":[{"Name":"iexplore.exe"},{"Name":"chrome.exe"}],"ConversionPath":"S:\\Peter Steciuk\\CALCULATORS"},"AdvancedSettingsModels":[],"Dropbox":{"AccessToken":"","AccessSecret":""},"SpreadsheetServer":{"Username":"","Password":"","ServerUrl":""},"ConfigureSubmitDefault":{"Email":"peter.steciuk@nepsi.com"}}
_Ctrl_2

## RVSS +actiVAR Calculations
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY
RVSS +actiVAR Performance Calculations & Graphs
Input Data |  |  | Per Unit Calculations and Calculated Results
| Motor HP: | 7000 |  | Motor KVA Rating: | 5383.5052
| Motor Voltage (kV): | 6.6 |  | Motor PU Impedance (XM): | 0.27825
| Motor Power Factor (%): | 100 |  | Transformer PU Impedance on Motor Base: | 0.030955
| Motor Efficiency (%): | 97 |  | Source PU Impedance on Motor Base: | 0.07178
| Lock Rotor kVA/HP: | 2.764 |  | Locked Rotor Amps With No Source Impedance: | 1694.5174 | RVSS Performance Showing Torque, Primary Voltage and Motor Bus (Secondary Bus) Voltage for Various RVSS Values | [8 empty] | RVSS & 11000 kvar actiVAR
| Source Short Circuit MVA at PCC: | 75 |  | Locked Rotor Amps in Per Unit: | 3.5939 | [12 empty] | Secondary Bus PU Voltage With 11000 kvar actiVAR | Primary Bus PU Voltage With 11000 kvar actiVAR
| Transformer MVA: | 10 |  | Max PU Locked Rotor Amps with Source Impedance: | 2.6248 | [9 empty] | actiVAR Rating to Fully Compensate for the RVSS Start (kvar) | Istart with 11000 kvar actiVAR (PU)* | Istart with 11000 kvar actiVAR (amps)**
| Transformer Impedance (%): | 5.75 |  | Maximum Starting Current (amps): | 1237.5747
| Per Unit Rated Starting Torque: | 0.7 |  | Full Load Amps: | 471.4928 | RVSS Setting (n)**** | [6 empty] | Primary Voltage Sag Limit | Secondary Voltage Sag Limit
| Primary Voltage Sag Limit (PU): | 0.96 |  | Per Unit Xc of actiVAR: | 0.53491 |  | Istart | PU of Rated Starting Torque*** | Starting Per Unit Torque* | Secondary Bus PU Voltage | Primary Bus PU Voltage | Istart
| Secondary Voltage Sag Limit (PU): | 0.8 |  |  |  |  | ILRA** |  |  |  |  | (amps)
| Enter actiVAR rating (kvar): | 11000 | (Enter kvar rating of actiVAR if one is to be used, otherwise enter 0) |  |  | 1e-06 | 1e-06 | 1e-12 | 7e-13 | 1 | 1 | 0.0016945 | 0.96 | 0.8 | 0.019348 | -2.3139 | -1090.9683 | 1.2377 | 1.1661
| actiVAR Voltage rating L-L (kV): | 6.9 |  |  |  | 0.05 | 0.049094 | 0.0024102 | 0.0016871 | 0.98187 | 0.98734 | 83.1901 | 0.96 | 0.8 | 967.4 | -2.0447 | -964.0755 | 1.2101 | 1.1468
| Enter proposed RVSS Setting: | 0.75 | (A value of 0 to 1.0 Per Unit) |  |  | 0.1 | 0.096439 | 0.0093005 | 0.0065104 | 0.96439 | 0.97512 | 163.418 | 0.96 | 0.8 | 1934.8 | -1.7874 | -842.7257 | 1.1836 | 1.1283
| Load Starting Torque: | 0.04 | (PU Based on Full Load Torque of Motor) |  |  | 0.15 | 0.14213 | 0.0202 | 0.01414 | 0.94752 | 0.96333 | 240.8391 | 0.96 | 0.8 | 2902.2 | -1.541 | -726.5658 | 1.1583 | 1.1106
[6 empty] | 0.2 | 0.18625 | 0.034688 | 0.024281 | 0.93123 | 0.95195 | 315.5982 | 0.96 | 0.8 | 3869.6 | -1.3049 | -615.2698 | 1.1341 | 1.0937
[6 empty] | 0.25 | 0.22887 | 0.052383 | 0.036668 | 0.91549 | 0.94096 | 387.8303 | 0.96 | 0.8 | 4837 | -1.0786 | -508.5384 | 1.1108 | 1.0774
[6 empty] | 0.3 | 0.27008 | 0.072945 | 0.051062 | 0.90028 | 0.93033 | 457.6613 | 0.96 | 0.8 | 5804.4 | -0.8613 | -406.0965 | 1.0885 | 1.0618
[6 empty] | 0.35 | 0.30995 | 0.096067 | 0.067247 | 0.88556 | 0.92004 | 525.2091 | 0.96 | 0.8 | 6771.8 | -0.65259 | -307.6907 | 1.067 | 1.0468
[6 empty] | 0.4 | 0.34853 | 0.12147 | 0.085029 | 0.87132 | 0.91009 | 590.5838 | 0.96 | 0.8 | 7739.2 | -0.45194 | -213.0869 | 1.0464 | 1.0324
[6 empty] | 0.45 | 0.38588 | 0.14891 | 0.10423 | 0.85752 | 0.90045 | 653.8886 | 0.96 | 0.8 | 8706.6 | -0.2589 | -122.069 | 1.0266 | 1.0186
[6 empty] | 0.5 | 0.42208 | 0.17815 | 0.12471 | 0.84416 | 0.89111 | 715.2203 | 0.96 | 0.8 | 9674 | -0.073038 | -34.4369 | 1.0075 | 1.0052
[6 empty] | 0.55 | 0.45716 | 0.209 | 0.1463 | 0.8312 | 0.88206 | 774.6698 | 0.96 | 0.8 | 10641.4 | 0.10604 | 49.9948 | 0.98911 | 0.99239
[6 empty] | 0.6 | 0.49119 | 0.24126 | 0.16888 | 0.81864 | 0.87329 | 832.3223 | 0.96 | 0.8 | 11608.8 | 0.27869 | 131.3984 | 0.97137 | 0.98
[6 empty] | 0.65 | 0.5242 | 0.27478 | 0.19235 | 0.80645 | 0.86477 | 888.2581 | 0.96 | 0.8 | 12576.2 | 0.44525 | 209.9338 | 0.95426 | 0.96804
[6 empty] | 0.7 | 0.55624 | 0.3094 | 0.21658 | 0.79462 | 0.85651 | 942.5528 | 0.96 | 0.8 | 13543.6 | 0.60605 | 285.7501 | 0.93774 | 0.9565
[6 empty] | 0.75 | 0.58735 | 0.34498 | 0.24149 | 0.78314 | 0.84848 | 995.2776 | 0.96 | 0.8 | 14511 | 0.76138 | 358.986 | 0.92178 | 0.94535
[6 empty] | 0.8 | 0.61758 | 0.3814 | 0.26698 | 0.77197 | 0.84068 | 1046.4995 | 0.96 | 0.8 | 15478.4 | 0.91151 | 429.771 | 0.90636 | 0.93457
[6 empty] | 0.85 | 0.64696 | 0.41855 | 0.29299 | 0.76113 | 0.8331 | 1096.2819 | 0.96 | 0.8 | 16445.8 | 1.0567 | 498.2263 | 0.89144 | 0.92415
[6 empty] | 0.9 | 0.67552 | 0.45633 | 0.31943 | 0.75058 | 0.82573 | 1144.6848 | 0.96 | 0.8 | 17413.2 | 1.1972 | 564.4648 | 0.87701 | 0.91407
[6 empty] | 0.95 | 0.70331 | 0.49464 | 0.34625 | 0.74032 | 0.81857 | 1191.7645 | 0.96 | 0.8 | 18380.6 | 1.3332 | 628.5927 | 0.86303 | 0.9043
[6 empty] | 1 | 0.73034 | 0.5334 | 0.37338 | 0.73034 | 0.81159 | 1237.5747 | 0.96 | 0.8 | 19348 | 1.4649 | 690.7092 | 0.8495 | 0.89485
[6 empty] | *Based on Full Load Torque Rating of Motor | [8 empty] | * Istart = Current Through Secondary of Service Transformer
[6 empty] | ** LRA = Locked Rotor Amps with No Source Impedance. Istart = Accounts for Source Impedance and RVSS Setting | [8 empty] | ** Negatigve Values of Istart means system is overcompensated by the actiVAR and is producing reactive power in excess of the RVSS setting. Choose a higher RVSS setting or consider a lower actiVAR reactive power rating.
*** Based on Per Unit Starting Torque as Read off of Torque Speed Curve at 0 Speed (locked Rotor Torque)
**** This represents the per unit of normal locked rotor current (no source impedance) or per unit voltage to motor during softstart
The following spreadsheet provides voltage sag mitigation performance and resulting motor torque for various values of current/voltage limitation by the RVSS. It also provides expected RVSS performance enhancements for an RVSS that is used in combination with an actiVARtm.
The actiVARtm extends the performance of the RVSS into larger motors and weaker power systems by supporting the primary and secondary voltage bus voltage during motor starts. When used in combination, the actiVARtm +RVSS provide soft mechanical starts, low harmonic current injection (as the actiVARtm filters while in the on state) and superior voltage sag performance.
The spreadsheet is a first order approximation of RVSS performance and RVSS +actiVAR performance based on motor and system inductive reactance (system resistance is ignored). All calculations are done in per unit on the motor’s kVA and voltage base.
Required Data: Motor nameplate data, motor starting torque (in per unit of full load torque), primary side short circuit level (in MVA), and service transformer nameplate data are required to obtain expected primary and secondary voltage sags levels at time of starting. NEPSI recommends a voltage sag no greater than 4% at the PCC and 10% at the motor during motor starting.
Since most medium voltage motor have stating torques of less the 1.0 PU, RVSS settings below 0.5 do not allow even the easiest loads to start.
The figure to the left shows a typical arrangement for an RVSS +actiVARTM application. The actiVARtm
can be sized smaller than a stand alone acitiVAR application as the RVSS mitigates a portion of the inrush current eleviating the requirement for a fully rated actiVARTM.
The use of an actiVARTM +RVSS system also allows for soft starting of the motor providing VFD start performance at a fraction of the cost of a VFD starter.
The actiVAR is designed for outdoor placement in the substation. Unlike VFD drives, it does not need an E-House, or SYNCH switchgear, and associated controls where multiple motors are to be started. Harmonics are not a concern as the actiVARTM filters and mitigates any hamronic concerns when the RVSS is in operation.
The actiVARTM can be packaged with RVSS starters as well as power factor correction capacitors/filters. The packageing of these components into a single piece of equipment reduces switchgear requirements, foot print area, engineering cost, procurement cost, and installation cost.
Check out http://nepsi.com/products/thyristor-switched-harmonic-filter-banks/ for more information on the actiVARTM, other calculators, spread sheet tools, case studies, as well as other NEPSI products.

## _Options (hidden)
.00001 | .00001 | .00001 | .00001 | .00001 | .00001
.1 | .1 | .1 | .1 | .1 | 0.1
.2 | .2 | .2 | .2 | .2 | 0.2
.3 | .3 | .3 | .3 | .3 | 0.3
.4 | .4 | .4 | .4 | .4 | 0.4
.5 | .5 | .5 | .5 | .5 | 0.5
.6 | .6 | .6 | .6 | .6 | 0.6
.7 | .7 | .7 | .7 | .7 | 0.7
.8 | .8 | .8 | .8 | .8 | 0.8
.9 | .9 | .9 | .9 | .9 | 0.9
| 1.0 | 1.0 | 1.0 | 1.0 | 1.0