## actiVAR Motor Start Calculation
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
actiVAR Performance Calculator
--------SOURCE DATA--------
SOURCE VOLTAGE (Kv LINE-TO-LINE): |  | 25 | CALCULATED
SOURCE 3-PHASE SHORT CIRCUIT CURRENT (kA): |  | 7 | Rpu | Xpu
X/R RATIO: |  | 10 | 0.0016632 | 0.016632
--------TRANSFORMER DATA--------
MVA RATING: |  | 30 | CALCULATED
PERCENT IMPEDANCE (ON TRANSFORMER BASE): |  | 7.5 | Rpu | Xpu
X/R RATIO: |  | 24 | 0.00052731 | 0.012656
--------MOTOR DATA--------
MOTOR VOLTAGE RATING (kV): |  | 4 | CALCULATED
FULL LOAD CURRENT RATING (FLA): |  | 731.3
LOCK ROTOR CURRENT (%): |  | 650
LOCK ROTOR PF (%): |  | 20 | Rpu | Xpu
MOTOR KVA BASE RATING: |  | 5066.5956 | 0.030769 | 0.15074
--------actiVAR™ DATA-------- |  |  |  |  | CAP/MOT EQIV.
actiVAR™ RATING (kV LINE-TO-LINE): |  | 4.16 | Rpu | Xpu | Rpu | Xpu
actiVAR™ RATING (MVAR THREE-PHASE): |  | 24 | 0 | -0.22833 | 0.23022 | 0.35227
actiVAR™ PERFORMANCE
| VMOTOR |  | VPRIMARY |  | TORQUE LOSS FROM VOLTAGE SAG (%) | actiVAR TORQUE ADVANTAGE (%)
| VOLTAGE DROP (%) | VOLTAGE SAG (%) | VOLTAGE DROP (%) | VOLTAGE SAG (%)
WITHOUT actiVAR™ | 15.9394 | 84.0606 | 9.1332 | 90.8668 | 29.3382
WITH actiVAR™ | 5.8062 | 94.1938 | 3.3596 | 96.6404 | 11.2753 | 18.0629
Motor Inrush Current
Inrush Current with actiVAR | 1636.8679 | amps | 2.2383 | Per Unit of FLA
Inrush Current without actiVAR | 3995.7787 | amps | 5.4639 | Per Unit of FLA
Use Locked-Rotor CODE on motor nameplate (KVA/HP) to determine Locked Rotor Current (%) for insertion in calculation above
Enter KVA/HP Based on Table 1: | 5.98
HP Rating of Motor (HP): | 5500
Enter Motor Terminal Voltage (kV): | 4
Enter FLA rating of Motor (Amps): | 731.3
Motor Inrush Current: | 4752.8902 | amps
Locked Rotor Current %: | 649.9%
The actiVAR reduces the inrush current from 3995.8 amps (5.5 Per Unit Current) to 1636.9 amps (2.2 Per Unit Current). The actiVAR decreases the voltage sag at the motor from 84.1% to 94.2%. The 25kV primary voltage sag is reduced from 90.9% to 96.6%.
The following calculator computes the expected performance of NEPSI's actiVAR™ in reducing voltage sags associated with large motor starts. Expected voltage sag, voltage drop, and inrush currents are calculated for "across-the-line motor starts" based on system impedance data and motor nameplate rating.
Known Variables: Source Data: Source Voltage, Source Short Circuit Level (in kA), and X/R Ratio
Supply Side Transformer Data: Transformer Power Rating (MVA), leakage impedance (in % on transformer base), and X/R ratio of leakage impedance Motor Nameplate Data: Motor voltage rating, motor full load current (FLA), motor locked rotor current (See code letters following calculator if not know), locked rotor power factor (assume 20% if not know)

## Voltage Resolution
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
actiVAR™ Voltage Resolution, Stage Sequence, Step & Stage Size Table
| Enter System Voltage: | 4.16 | kV
| Enter total kvar required by actiVAR: | 24000 | kvar
| Calculated MVAsc at actiVAR: | 172.5105 | MVA
Number of Steps | Number of Stages | Stage Sequence | Smallest Step Size | Required DS1M Rating Stage (amps)* | Approximate Voltage Resolution
1 | 1 | 1 | 24000 | 3334.8155 | ± 6.96%
2 | 2 | 1:1 | 12000 | 1667.4077 | ± 3.48%
3 | 3 | 1:1:1 | 8000 | 1111.6052 | ± 2.32%
4 | 4 | 1:1:1:1 | 6000 | 833.7039 | ± 1.74%
5 | 5 | 1:1:1:1:1 | 4800 | 666.9631 | ± 1.39%
6 | 6 | 1:1:1:1:1:1 | 4000 | 555.8026 | ± 1.16%
7 | 7 | 1:1:1:1:1:1:1 | 3428.5714 | 476.4022 | ± 0.99%
8 | 8 | 1:1:1:1:1:1:1:1 | 3000 | 416.8519 | ± 0.87%
* Current Rating of ABB DS1M: ≈ 444 Amps, values colored red are not valid ratings

## Sheet1
Load
5000
5000
5000
5000
1500
1500
1500
1500
500
500
500
2000
2000
31500

## _SSC (hidden)
_Ctrl_1 | {"WidgetClassification":0,"State":1,"SliderFlavor":1,"MinValue":0,"MaxValue":100,"TickInterval":0,"ShowTextbox":false,"ShowValueInTooltip":true,"IsRangeSlider":false,"CellName":"_Ctrl_1","CellAddress":"='Sheet1'!$J$7","WidgetName":6,"HiddenRow":1,"SheetCodeName":null,"ControlId":null} | {"IsHide":true,"SheetId":0,"Name":"actiVAR Motor Start Calculation","HiddenRow":0,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}} | {"ButtonStyle":0,"Name":"","HideSscPoweredlogo":false,"CopyProtect":{"IsEnabled":false,"DomainName":""},"Theme":{"BgColor":"#FFFFFFFF","BgImage":"","InputBorderStyle":2},"Layout":0,"SmartphoneSettings":{"ViewportLock":true,"UseOldViewEngine":false,"EnableZoom":false,"EnableSwipe":false,"HideToolbar":false,"InheritBackgroundColor":false,"CheckboxFlavor":1},"SmartphoneTheme":0,"InputDetection":1,"Toolbar":{"Position":1,"IsSubmit":false,"IsPrint":true,"IsPrintAll":false,"IsReset":true,"IsUpdate":false},"AspnetConfig":{"BrowseUrl":"http://localhost/ssc","FileExtension":0},"ConfigureSubmit":{"IsShowCaptcha":false,"IsUseSscWebServer":true,"ReceiverCode":"peter.steciuk@nepsi.com","IsFreeService":false,"IsAdvanceService":true,"IsDemonstrationService":false,"AfterSuccessfulSubmit":"","AfterFailSubmit":"","AfterCancelWizard":"","IsUseOwnWebServer":false,"OwnWebServerURL":"","OwnWebServerTarget":"","SubmitTarget":0},"Flavor":0,"Edition":3,"IgnoreBgInputCell":false} | {"Captcha":{"Heading":"Enter the number displayed below.","Message":"This is to verify that you are a human visitor, to prevent automated form submissions.","OkButton":"OK","CancelButton":"Cancel","ErrorMessage":"Your answer is incorrect, please try again."},"RequiredField":{"ErrorMessage":"The fields with the red border are required.","OkButton":"OK","DDLDefaultRequiredText":"Please Select"},"WizardButton":{"Next":"Next","Previous":"Previous","Cancel":"Cancel","Finish":"Finish"},"ToolbarButton":{"Submit":"Submit","Print":"Print","PrintAll":"Print All","Reset":"Reset","Update":"Update","Back":"Back"},"BrowserAndLocation":{"Browsers":[{"Name":"iexplore.exe"},{"Name":"chrome.exe"}],"ConversionPath":"S:\\Peter Steciuk\\CALCULATORS"},"AdvancedSettingsModels":[],"Dropbox":{"AccessToken":"","AccessSecret":""},"SpreadsheetServer":{"Username":"","Password":"","ServerUrl":""},"ConfigureSubmitDefault":{"Email":"peter.steciuk@nepsi.com"}}
{"IsHide":true,"SheetId":0,"Name":"Voltage Resolution ","HiddenRow":0,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":0,"Name":"Sheet1","HiddenRow":0,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}