## Spread Sheet
Check out this YouTube video that discusses Transient Inrush Currents
https://youtu.be/zUPDfCfcF_4
Northeast Power Systems, Inc.
| 66 Carey Road, Queensbury, NY | [5 empty] | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
CALCULATION OF PEAK INRUSH CURRENT FOR ISOLATED AND BACK-TO-BACK CAPACITOR BANK SWITCHING
Input Capacitor Bank Voltage (kVLL): | [6 empty] | 38 |  | Project Name: |  |  | Project Name
Input Short Circuit Current Level at Capacitor Bank (kA): | [6 empty] | 10
Input System Frequency (Hz): | [6 empty] | 60
[8 empty] | Single Stage |  | Single Stage |  |  | Back-to-Back |  |  | Back-to-Back
|  |  | Reactive Power | Stage |  | Stage |  | Inrush Current |  | Inrush Frequency |  |  | Inrush Current |  |  | Inrush Frequency | Product I x f
|  | Stage # | Rating (kvar) | Inductance (µH) |  | Current (amps) |  | (amps-peak) |  | (Hz) |  |  | (amps-peak) |  |  | (kHz) | kAHz
|  | Stage 1 | 1000 | 80 |  | 15.2114 |  | 547.8162 |  | 1527.9352 |  |  | n/a |  |  | n/a | 837.0276
|  | Stage 2 | 1000 | 80 |  | 15.2114 |  | n/a |  | n/a |  |  | 2342.3948 |  |  | 13.0035 | 30459.375
|  | Stage 3 | 1000 | 80 |  | 15.2114 |  | n/a |  | n/a |  |  | 3123.1931 |  |  | 13.0035 | 40612.5
|  | Stage 4 | 0 | 0 |  | 0 |  | n/a |  | n/a |  |  | n/a |  |  | n/a | n/a
|  | Stage 5 | 0 | 0 |  | 0 |  | n/a |  | n/a |  |  | n/a |  |  | n/a | n/a
|  | Stage 6 | 0 | 0 |  | 0 |  | n/a |  | n/a |  |  | n/a |  |  | n/a | n/a
|  | Stage 7 | 0 | 0 |  | 0 |  | n/a |  | n/a |  |  | n/a |  |  | n/a | n/a
|  | Stage 8 | 0 | 0 |  | 0 |  | n/a |  | n/a |  |  | n/a |  |  | n/a | n/a
[5 empty] | Switching Device: | HD4, 31.5Ka, 1200 Amp
[5 empty] | Peak Transient Making Current (amps-peak): | 20000 | [7 empty] | Within Switch Rating ?: | Yes - Max is 7808
[5 empty] | Peak Transient Making Frequency (kHz): | 4.25 |  |  |  |  | Within Switch Rating ?: |  |  |  | No, but very close. IxF is more important to meet
[5 empty] | Product I x F rating of Switch (kAHz) | 85000 |  |  |  |  | Within Switch Rating ?: |  |  |  | Yes - Max is 85000
Reference Formulas and Variables from IEEE C37.012-20-05
Peak Inrush Current Calculation
| 66 Carey Road, Queensbury, NY | [5 empty] | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
This spread sheet computes the expected transient inrush current associated with isolated and back-to-back capacitor bank switching. Input the stage reactive power rating, stage inductance, capacitor bank voltage rating, system frequency, and the short circuit level at the capacitor bank. The spread sheet provides the expected single stage inrush current as well as back-to-back inrush current magnitude and frequency for single stage and multi-stage capacitor banks. The calculations are based on IEEE C37.012-2005, Application Guide for Capacitance Current Switching for AC High-Voltage Circuit Breakers.
Back Ground Information
Single stage and multi-stage capacitor banks, when energized, draw significant amounts of inrush current. This inrush current must be considered when choosing the capacitor switching device and transient inrush reactor. Two types of switching events, as defined by IEEE C37.012-2005 are as follows:
  * The capacitor bank is energized from a bus that does not have other capacitor banks energized. This situation is called isolated capacitor bank switching.
  * The capacitor bank is energized from a bus that has other capacitor banks energized. This situation is called back-to-back capacitor bank switching.
A capacitor bank is considered isolated when the inrush current on energization is limited by the inductance of the source and the capacitance of the bank being energized. The inrush current of an isolated capacitor bank will be increased when other capacitor banks are connected to the same bus or nearby. Such a case always exists in multi-stage capacitor bank and also in substations where multiple capacitor banks may be applied on opposite sides of a tie-breaker. Such applications give rise to an inrush current of very high amplitude and frequency, which has to be limited in order not to be harmful to the circuit breaker or capacitor switch, the capacitor banks, and/or the network. The magnitude and frequency of this inrush current is a function of the following:
  1) Applied voltage (point on the voltage wave at closing)
  2) Capacitance of the circuit
  3) Inductance in the circuit (amount and location)
  4) Any charge on the capacitor bank at the instant of closing
  5) Any damping of the circuit due to closing resistors, e.g., a Southern States CapSwitcher, or other resistances in the circuit
It is assumed that the capacitor bank is discharged prior to energization. This assumption is reasonable, as capacitor units are fitted with discharging resistors that will discharge the capacitor bank. Typical discharge times are on the order of 5 min. The transient inrush current to an isolated bank is less than the available short-circuit current at the capacitor bank terminals. It rarely exceeds 20 times the rated current of the capacitor bank at a frequency that approaches 1 kHz. Because a circuit breaker must meet the making current requirements of the system, transient inrush current is not a limiting factor in isolated capacitor bank applications. When capacitor banks are switched back-to-back (i.e., when one bank is switched while another bank is connected to the same bus), transient currents of prospective high magnitude and frequency flow between the banks on closing of the circuit breaker or capacitor switch. The effects are similar to that of a restrike on opening. This oscillatory current that follows is limited only by the impedance of the capacitor bank and the circuit impedance between the energized bank or banks and the switched bank. This transient current usually decays to zero in a fraction of a cycle of the system frequency. In the case of back-to-back switching, the component supplied by the source is at a lower frequency; therefore it is normally neglected.
For General Purpose Circuit Breakers (Class C0), the transient inrush peak current on closing is to be less than 1.41 times the rated short circuit current or 50kA (whichever is less) and the product of the inrush current peak and frequency shall not exceed 20,000 kAHz.
For vacuum switches not covered by IEEE C37.06, but rather by C37.66, IEEE standard for capacitor switches, NEPSI recommends the inrush current magnitude be limited to 50% of the switch high frequency making current rating. Such a recommendation ensures long life and trouble free operation of the switching device.
X

## PES-TR16
NEPSI's experience: 2.4kV through 15kV rated capacitor banks typically have transient inrush reactors rated as low as 40 micro-Henrys. At 38kV, their values typically increase to near 100 micro-Henrys. Their current rating should account for maxium system voltage including over-voltages.

## C37.06 - 2009
Note Paragraph to left for general purpose breakers.
Note current inrush peak and frequency may break from preferred standard values.
Note Paragraph to left for C1 and C2 rated breakers. (The peak withstand and close & latch rating = 2.6 x breaker sym. short circuit rating)

## IEEE Std. 1036-2010
For outrush concerns, consult NEPSI spread sheet tool at the following address:
http://nepsi.com/resource/Peak-Capacitor-Bank-Out-Rush-Current-Calculation.xlsx

## _SSC (hidden)
{"IsHide":false,"SheetId":0,"Name":"Sheet1","HiddenRow":0,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}} | {"ButtonStyle":0,"Name":"","HideSscPoweredlogo":false,"CopyProtect":{"IsEnabled":false,"DomainName":""},"Theme":{"BgColor":"#FFFFFFFF","BgImage":"","InputBorderStyle":2},"Layout":0,"SmartphoneSettings":{"ViewportLock":true,"UseOldViewEngine":false,"EnableZoom":false,"EnableSwipe":false,"HideToolbar":false,"InheritBackgroundColor":false,"CheckboxFlavor":1},"SmartphoneTheme":0,"InputDetection":0,"Toolbar":{"Position":1,"IsSubmit":true,"IsPrint":true,"IsPrintAll":false,"IsReset":true,"IsUpdate":true},"AspnetConfig":{"BrowseUrl":"http://localhost/ssc","FileExtension":0},"ConfigureSubmit":{"IsShowCaptcha":false,"IsUseSscWebServer":true,"ReceiverCode":"peter.steciuk@nepsi.com","IsFreeService":false,"IsAdvanceService":true,"IsDemonstrationService":false,"AfterSuccessfulSubmit":"","AfterFailSubmit":"","AfterCancelWizard":"","IsUseOwnWebServer":false,"OwnWebServerURL":"","OwnWebServerTarget":"","SubmitTarget":0},"Flavor":0,"Edition":3,"IgnoreBgInputCell":false} | {"Captcha":{"Heading":"Enter the number displayed below.","Message":"This is to verify that you are a human visitor, to prevent automated form submissions.","OkButton":"OK","CancelButton":"Cancel","ErrorMessage":"Your answer is incorrect, please try again."},"RequiredField":{"ErrorMessage":"The fields with the red border are required.","OkButton":"OK","DDLDefaultRequiredText":"Please Select"},"WizardButton":{"Next":"Next","Previous":"Previous","Cancel":"Cancel","Finish":"Finish"},"ToolbarButton":{"Submit":"Submit","Print":"Print","PrintAll":"Print All","Reset":"Reset","Update":"Update","Back":"Back"},"BrowserAndLocation":{"Browsers":[{"Name":"iexplore.exe"},{"Name":"chrome.exe"}],"ConversionPath":"S:\\Peter Steciuk\\CALCULATORS"},"AdvancedSettingsModels":[],"Dropbox":{"AccessToken":"","AccessSecret":""},"SpreadsheetServer":{"Username":"","Password":"","ServerUrl":""},"ConfigureSubmitDefault":{"Email":"peter.steciuk@nepsi.com"}}
{"IsHide":true,"SheetId":0,"Name":"Sheet2","HiddenRow":0,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":0,"Name":"Sheet3","HiddenRow":0,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}